## Table 3
FEEDER SCHEDULE FX00A
TAG | OCPD AMPS | COPPER |  |  |  | ALUMINUM
|  | SETS, # OF CONDUCTORS, CONDUIT |  |  |  | SETS, # OF CONDUCTORS, CONDUIT
F20 | 20 | 1 | 3 #12 | 1#12 G | 3/4" C
F20N |  | 1 | 4 #12 | 1#12 G | 3/4" C
F30 | 30 | 1 | 3 #10 | 1#10 G | 3/4" C
F30N |  | 1 | 4 #10 | 1#10 G | 3/4" C
F40 | 40 | 1 | 3 #8 | 1#10 G | 1" C
F40N |  | 1 | 4 #8 | 1#10 G | 1" C
F45 | 45 | 1 | 3 #6 | 1#10 G | 1" C
F45N |  | 1 | 4 #6 | 1#10 G | 1" C
F50 | 50 | 1 | 3 #6 | 1#10 G | 1" C
F50N |  | 1 | 4 #6 | 1#10 G | 1" C
F60 | 60 | 1 | 3 #4 | 1#10 G | 1-1/4" C
F60N |  | 1 | 4 #4 | 1#10 G | 1-1/4" C
F70 | 70 | 1 | 3 #4 | 1#8 G | 1-1/4" C
F70N |  | 1 | 4 #4 | 1#8 G | 1-1/4" C
F80 | 80 | 1 | 3 #3 | 1#8 G | 1-1/4" C
F80N |  | 1 | 4 #3 | 1#8 G | 1-1/4" C
F90 | 90 | 1 | 3 #2 | 1#8 G | 1-1/4" C
F90N |  | 1 | 4 #2 | 1#8 G | 1-1/4" C
F100 | 100 | 1 | 3 #1 | 1#8 G | 1-1/2" C | 1 | 3 #1/0 | 1#6 G | 1-1/2" C
F100N |  | 1 | 4 #1 | 1#8 G | 2" C | 1 | 4 #1/0 | 1#6 G | 2" C
F110 | 110 | 1 | 3 #1 | 1#6 G | 1-1/2" C | 1 | 3 #1/0 | 1#4 G | 2" C
F110N |  | 1 | 4 #1 | 1#6 G | 2" C | 1 | 4 #1/0 | 1#4 G | 2" C
F125 | 125 | 1 | 3 #1 | 1#6 G | 1-1/2" C | 1 | 3 #2/0 | 1#4 G | 2" C
F125N |  | 1 | 4 #1 | 1#6 G | 2" C | 1 | 4 #2/0 | 1#4 G | 2" C
F150 | 150 | 1 | 3 #1/0 | 1#6 G | 2" C | 1 | 3 #3/0 | 1#4 G | 2" C
F150N |  | 1 | 4 #1/0 | 1#6 G | 2" C | 1 | 4 #3/0 | 1#4 G | 2" C
F175 | 175 | 1 | 3 #2/0 | 1#6 G | 2" C | 1 | 3 #4/0 | 1#4 G | 2" C
F175N |  | 1 | 4 #2/0 | 1#6 G | 2" C | 1 | 4 #4/0 | 1#4 G | 2-1/2" C
F200 | 200 | 1 | 3 #3/0 | 1#6 G | 2" C | 1 | 3 #250KCMIL | 1#4 G | 2-1/2" C
F200N |  | 1 | 4 #3/0 | 1#6 G | 2-1/2" C | 1 | 4 #250KCMIL | 1#4 G | 2-1/2" C
F225 | 225 | 1 | 3 #4/0 | 1#4 G | 2-1/2" C | 1 | 3 #300KCMIL | 1#2 G | 2-1/2" C
F225N |  | 1 | 4 #4/0 | 1#4 G | 2-1/2" C | 1 | 4 #300KCMIL | 1#2 G | 2-1/2" C
F250 | 250 | 1 | 3 #250KCMIL | 1#4 G | 2-1/2" C | 1 | 3 #350KCMIL | 1#2 G | 2-1/2" C
F250N |  | 1 | 4 #250KCMIL | 1#4 G | 2-1/2" C | 1 | 4 #350KCMIL | 1#2 G | 3" C
F300 | 300 | 1 | 3 #350KCMIL | 1#4 G | 3" C | 1 | 3 #500KCMIL | 1#2 G | 3" C
F300N |  | 1 | 4 #350KCMIL | 1#4 G | 3" C | 1 | 4 #500KCMIL | 1#2 G | 3-1/2" C
F350 | 350 | 1 | 3 #500KCMIL | 1#3 G | 3" C | 1 | 3 #700KCMIL | 1#1 G | 3-1/2" C
F350N |  | 1 | 4 #500KCMIL | 1#3 G | 3" C | 1 | 4 #700KCMIL | 1#1 G | 4" C
F400 | 400 | 1 | 3 #600KCMIL | 1#3 G | 3-1/2" C | 2 | 3 #250KCMIL | 1#1 G | 3" C
F400N |  | 1 | 4 #600KCMIL | 1#3 G | 3-1/2" C | 2 | 4 #250KCMIL | 1#1 G | 3" C
F450 | 450 | 2 | 3 #4/0 | 1#2 G | 2" C | 2 | 3 #300KCMIL | 1#1/0 G | 2-1/2" C
F450N |  | 2 | 4 #4/0 | 1#2 G | 2-1/2" C | 2 | 4 #300KCMIL | 1#1/0 G | 3" C
F500 | 500 | 2 | 3 #250KCMIL | 1#2 G | 2-1/2" C | 2 | 3 #350KCMIL | 1#1/0 G | 2-1/2" C
F500N |  | 2 | 4 #250KCMIL | 1#2 G | 2-1/2" C | 2 | 4 #350KCMIL | 1#1/0 G | 3" C
F600 | 600 | 2 | 3 #350KCMIL | 1#1 G | 2-1/2" C | 2 | 3 #500KCMIL | 1#2/0 G | 3" C
F600N |  | 2 | 4 #350KCMIL | 1#1 G | 3" C | 2 | 4 #500KCMIL | 1#2/0 G | 3-1/2" C
F700 | 700 | 2 | 3 #500KCMIL | 1#1/0 G | 3" C | 2 | 3 #700KCMIL | 1#3/0 G | 3-1/2" C
F700N |  | 2 | 4 #500KCMIL | 1#1/0 G | 3-1/2" C | 2 | 4 #700KCMIL | 1#3/0 G | 4" C
F800 | 800 | 2 | 3 #600KCMIL | 1#1/0 G | 3-1/2" C | 3 | 3 #400KCMIL | 1#3/0 G | 3" C
F800N |  | 2 | 4 #600KCMIL | 1#1/0 G | 4" C | 3 | 4 #400KCMIL | 1#3/0 G | 3" C
F1000 | 1000 | 3 | 3 #400KCMIL | 1#2/0 G | 3" C | 3 | 3 #600KCMIL | 1#4/0 G | 3-1/2" C
F1000N |  | 3 | 4 #400KCMIL | 1#2/0 G | 3" C | 3 | 4 #600KCMIL | 1#4/0 G | 4" C
F1200 | 1200 | 3 | 3 #600KCMIL | 1#3/0 G | 3-1/2" C | 4 | 3 #500KCMIL | 1#250KCMIL G | 3" C
F1200N |  | 3 | 4 #600KCMIL | 1#3/0 G | 4" C | 4 | 4 #500KCMIL | 1#250KCMIL G | 3-1/2" C
F1600 | 1600 | 4 | 3 #600KCMIL | 1#4/0 G | 3-1/2" C | 5 | 3 #600KCMIL | 1#350KCMIL G | 3-1/2" C
F1600N |  | 4 | 4 #600KCMIL | 1#4/0 G | 4" C | 5 | 4 #600KCMIL | 1#350KCMIL G | 4" C
F2000 | 2000 | 5 | 3 #600KCMIL | 1#250KCMIL G | 3-1/2" C | 6 | 3 #600KCMIL | 1#400KCMIL G | 3-1/2" C
F2000N |  | 5 | 4 #600KCMIL | 1#250KCMIL G | 4" C | 6 | 4 #600KCMIL | 1#400KCMIL G | 4" C
F2500 | 2500 | 6 | 3 #600KCMIL | 1#350KCMIL G | 3-1/2" C | 7 | 3 #700KCMIL | 1#600KCMIL G | 3-1/2" C
F2500N |  | 6 | 4 #600KCMIL | 1#350KCMIL G | 4" C | 7 | 4 #700KCMIL | 1#600KCMIL G | 4" C
F3000 | 3000 | 8 | 3 #500KCMIL | 1#400KCMIL G | 3-1/2" C | 8 | 3 #700KCMIL | 1#600KCMIL G | 3-1/2" C
F3000N |  | 8 | 4 #500KCMIL | 1#400KCMIL G | 3-1/2" C | 8 | 4 #700KCMIL | 1#600KCMIL G | 4" C
F3500 | 3500 | 9 | 3 #600KCMIL | 1#500KCMIL G | 3-1/2" C | 10 | 3 #700KCMIL | 1#750KCMIL G | 3-1/2" C
F3500N |  | 9 | 4 #600KCMIL | 1#500KCMIL G | 4" C | 10 | 4 #700KCMIL | 1#750KCMIL G | 4" C
F4000 | 4000 | 10 | 3 #600KCMIL | 1#500KCMIL G | 3-1/2" C | 11 | 3 #700KCMIL | 1#750KCMIL G | 3-1/2" C
F4000N |  | 10 | 4 #600KCMIL | 1#500KCMIL G | 4" C | 11 | 4 #700KCMIL | 1#750KCMIL G | 4" C
NOTES: 1. THIS TABLE IS BASED ON CONDUCTORS IN ELECTRIC METAL TUBING CONDUIT (EMT) AND FOR THE LENGTH OF MAXIMUM 100 FEET FOR 208V, 3 PHASE, 4 WIRE AND 200 FEET FOR 480V, 3 PHASE, 4 WIRE SYSTEM. CONDUCTORS SHALL BE XHWN/XHHN FOR UNDERGROUND AND WERE SUBJECT TO MOISTURE, ALL OTHER INDOOR LOCATIONS SHALL USE THHN/THWN CONDUCTORS. ALL CABLES IN THE RACEWAYS EXPOSED TO SUNLIGHT SHALL BE XHHW-2. 1.1. AT NO COST TO THE OWNER, CONDUIT SIZE SHALL BE ADJUSTED AS PER NATIONAL ELECTRICAL CODE WHEN PROVIDED CONDUIT IS NOT EMT. 1.2. AT NO COST TO THE OWNER, WIRING SHALL BE MODIFIED AS PER NATIONAL ELECTRICAL CODE AS REQUIRED TO COMPLY WITH VOLTAGE DROP LIMITATIONS, INCLUDING MODIFICATIONS TO THE CONDUIT SIZE WHERE REQUIRED. 2. ALUMINUM CONDUCTORS ARE PERMITTED ONLY WITH OWNER APPROVAL AND FOR FEEDERS RATED 100A OR LARGER. 2.1. ALUMINUM FEEDERS MUST BE TERMINATED UTILIZING COMPRESSION TYPE CONNECTORS. 3. ANY DISCREPANCY BETWEEN SIZES INDICATED IN THIS TABLE AND SIZES REQUIRED BY NATIONAL ELECTRICAL CODE, NATIONAL CODE SHALL GOVERN. 4. OVERCURRENT PROTECTION DEVICES (OCPD) AMPACITY SHALL BE USED FOR FEEDER SIZING, UNLESS INDICATED OTHERWISE ELSEWHERE IN CONTRACT DOCUMENTS. ANY DISCREPANCIES SHALL BE BROUGHT UP TO IMMEDIATE ATTENTION OF THE ENGINEER. 5. FEEDERS SHALL BE COMPATIBLE WITH EQUIPMENT LUG RATING AND MATERIAL 6. WHERE UNGROUNDED CONDUCTORS ARE INCREASED IN SIZE FROM WHAT SHOWN IN THE TABLE ABOVE, GROUNDING CONDUCTOR(S) SHALL BE INCREASED IN SIZE PROPORTIONALLY ACCORDING TO THE CIRCULAR MIL AREA OF THE UNGROUNDED CONDUCTORS.
FX00A